## Three_bus_without_transients
On the importance of considering dynamic changes on network topology on the optimal coordination of overcurrent protections, submitted to IJEPES
Paulo M. De Oliveira-De Jesus & Alberto J. Urdaneta
Example 1.2 | [14 empty] | IEC 60255 SI Curve
Fault | relay |  | relay |  | buses |  | buses |  | Icc,0 (kA) |  | b_0 |  | q_cc,0 (deg) |  | a1= | 0.14
location | back | line | main | line | from | to | from | to | main | back | main | back | main | back | a2= | 0.02
Near-end | 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 4.9936 | 0.81939 | 2.4199 | 2.9393 | -88.4646 | -80.604
Near-end | 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 2.775 | 1.0377 | 2.5921 | 5.5708 | -87.1309 | -82.3079 |  | Pick-up settings
Near-end | 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 4.5679 | 2.2468 | 1.6616 | 2.8244 | -87.9404 | -85.8103 | 1 | 0.3
[15 empty] | 2 | 0.06
[15 empty] | 3 | 0.2
[15 empty] | 4 | 0.24
[15 empty] | 5 | 0.08
[15 empty] | 6 | 0.2
Far-end | 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 4.2734 | 2.5331 | 1.5719 | 2.901 | -87.4617 | -85.7155
Far-end | 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 3.1876 | 0.87257 | 2.6371 | 4.6821 | -87.3394 | -80.2369
Far-end | 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 5.1333 | 0.95623 | 2.0878 | 2.459 | -88.6474 | -82.722
Objective function
[9 empty] | B | [5 empty] | D |  | S
[8 empty] | 1 | -2.4199 | 0 | 0 | 0 | 2.9393 | 0 | 0.11292 |  | 0.2 | T111= | 0.27326
[8 empty] | 2 | 0 | -1.5719 | 0 | 2.901 | 0 | 0 | 0.20324 |  | 0.2 | T222= | 0.31948
[8 empty] | 3 | 5.5708 | 0 | -2.5921 | 0 | 0 | 0 | 0.16553 | = | 0.2 | T331= | 0.42908
[8 empty] | 4 | 0 | 0 | 0 | -2.6371 | 0 | 4.6821 | 0.17907 |  | 0.2 | T412= | 0.47222
[8 empty] | 5 | 0 | 0 | 2.8244 | 0 | -1.6616 | 0 | 0.16101 |  | 0.2 | T521= | 0.26753
[8 empty] | 6 | 0 | 2.459 | 0 | 0 | 0 | -2.0878 | 0.14357 |  | 0.2 | T632= | 0.29975
[18 empty] | T = | 2.0613
Bus 4
G1
Line 1
G2
G3
Line 2
Line 3
Bus 1
Bus 2
Bus 3
Bus 5
Bus 6

## Three_bus_with_transients
On the importance of considering dynamic changes on network topology on the optimal coordination of overcurrent protections, submitted to IJEPES | [24 empty] | IEC 60255 SI Curve
Paulo M. De Oliveira-De Jesus & Alberto J. Urdaneta | [24 empty] | a1= | 0.14
Example 1.2 | [24 empty] | a2= | 0.02
Fault | relay |  | relay |  | buses |  | buses |  | Icc,0 (kA) |  | Icc,1 (kA) |  | b_0 |  | b_1 |  | q_cc,0 (deg) |  | q_cc,1 (deg) |  |  | relay
location | back | line | main | line | from | to | from | to | main | back | main | back | main | back | main | back | main | back | main | back | g_type_2 | u | line | g_type_3 |  | Pick-up settings
Near-end | 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 4.9936 | 0.81939 | 5.2129 | 1.047 | 2.4199 | 2.9393 | 2.3824 | 2.6526 | -88.4646 | -80.604 | -87.6684 | -78.3143 | -0.20176 | 2 | 1 | -2.4208 | 1 | 0.3
Near-end | 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 2.775 | 1.0377 | 3.0056 | 1.2749 | 2.5921 | 5.5708 | 2.5138 | 4.7684 | -87.1309 | -82.3079 | -85.535 | -79.4247 | -0.33016 | 4 | 2 | -2.8132 | 2 | 0.06
Near-end | 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 4.5679 | 2.2468 | 4.7672 | 2.4488 | 1.6616 | 2.8244 | 1.6435 | 2.7249 | -87.9404 | -85.8103 | -87.1169 | -84.3812 | -0.11392 | 6 | 3 | -4.6311 | 3 | 0.2
Near-end | 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 0.95629 | 0.18354 | 1.2334 | 0.75459 | 2.4589 | -26.1674 | 2.2462 | 6.0409 | -82.7225 | -85.6353 | -79.2375 | -77.0587 | -2.7692 | 1 | 1 | -2.2105 | 4 | 0.24
Near-end | 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 2.5332 | 0.61921 | 2.7676 | 0.90164 | 2.9009 | 6.1243 | 2.7934 | 4.5787 | -85.7158 | -78.6578 | -84.0832 | -75.5994 | -0.55808 | 3 | 2 | -2.496 | 5 | 0.08
Near-end | 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 0.87259 | 0.77631 | 1.1273 | 0.24752 | 4.6821 | 2.6647 | 3.9783 | 4.8699 | -80.237 | 98.8039 | -77.125 | -69.5875 | 1.6247 | 5 | 3 | -1.4118 | 6 | 0.2
Far-end | 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 1.0378 | 0.61918 | 1.2837 | 0.25781 | 5.5707 | 3.3512 | 4.7457 | 5.9122 | -82.3079 | 101.3425 | -79.2083 | -69.8542 | 1.4341 | 2 | 1 | -1.3391
Far-end | 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 2.2469 | 0.77635 | 2.4892 | 1.0559 | 2.8243 | 7.2923 | 2.7068 | 5.4931 | -85.8107 | -81.1965 | -83.9316 | -77.8214 | -0.54091 | 4 | 2 | -2.5274
Far-end | 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 0.81944 | 0.18348 | 1.0991 | 0.56461 | 2.9392 | -81.2766 | 2.6021 | 6.6752 | -80.6044 | 94.3652 | -77.2156 | -74.4799 | -2.0198 | 6 | 3 | -1.8483
Far-end | 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 4.2734 | 2.5331 | 4.4773 | 2.7393 | 1.5719 | 2.901 | 1.5542 | 2.8055 | -87.4617 | -85.7155 | -86.5746 | -84.3958 | -0.12043 | 1 | 1 | -5.5079
Far-end | 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 3.1876 | 0.87257 | 3.4205 | 1.1143 | 2.6371 | 4.6821 | 2.5653 | 4.0056 | -87.3394 | -80.2369 | -85.9439 | -77.4601 | -0.33116 | 3 | 2 | -2.7474
Far-end | 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 5.1333 | 0.95623 | 5.3436 | 1.1733 | 2.0878 | 2.459 | 2.0614 | 2.2851 | -88.6474 | -82.722 | -87.8912 | -80.3537 | -0.17075 | 5 | 3 | -2.9021
Objective function
| Constraint type: | [7 empty] | B | [5 empty] | D |  | S
| Type 3 q-r pair |  |  | relay q stuck in period 1 |  |  |  | 1 | 2.2105 | -2.2462 | 0 | 6.0409 | 0 | 0 | 0.11292 |  | 0.88396 | T212_0= | 0.33339
| Type 1 w-u pair | [6 empty] | 2 | -2.4199 | 0 | 0 | 0 | 2.9393 | 0 | 0.21209 |  | 0.2 | T111_0= | 0.27326
| Type 2 q-r pair | [6 empty] | 3 | 0 | 0 | 0.55808 | -2.7934 | 0 | 4.5787 | 0.16553 | = | 0.28387 | T422_0= | 0.48487
| Type 1 w-u pair | [6 empty] | 4 | 5.5708 | 0 | -2.5921 | 0 | 0 | 0 | 0.18387 |  | 0.2 | T321_0= | 0.42908
| Type 3 q-r pair |  |  | relay q stuck in period 1 |  |  |  | 5 | 0 | 4.8699 | 0 | 0 | 1.4118 | -3.9783 | 0.16101 |  | 0.64751 | T632_0= | 0.32151
| Type 1 w-u pair | [6 empty] | 6 | 0 | 0 | 2.8244 | 0 | -1.6616 | 0 | 0.15399 |  | 0.2 | T531_0= | 0.26753
| Type 3 q-r pair |  |  | relay q stuck in period 1 |  |  |  | 7 | -4.7457 | 1.3391 | 0 | 0 | 5.9122 | 0 |  |  | 0.70004
| Type 1 w-u pair | [6 empty] | 8 | 0 | -1.5719 | 0 | 2.901 | 0 | 0 |  |  | 0.2
| Type 2 q-r pair | [6 empty] | 9 | 0 | 0 | 0.33116 | -2.5653 | 0 | 4.0056 |  |  | 0.2
| Type 1 w-u pair | [6 empty] | 10 | 7.2923 | 0 | -2.8243 | 0 | 0 | 0 |  |  | 0.35595
| Type 3 q-r pair |  |  | relay q stuck in period 1 |  |  |  | 11 | 0 | 0 | 6.6752 | 0 | -2.6021 | 1.8483 |  |  | 0.97064
| Type 1 w-u pair | [6 empty] | 12 | 0 | 2.459 | 0 | 0 | 0 | -2.0878 |  |  | 0.2
[19 empty] | Td= | 2.1096
Bus 4
G1
Line 1
G2
G3
Line 2
Line 3
Bus 1
Bus 2
Bus 3
Bus 5
Bus 6