## RF=0 and 10
IEC 60255 SI Curve
[26 empty] | a1= | 0.14
[17 empty] | First Period |  | Second Period | [6 empty] | a2= | 0.02
Fault | relay |  | relay |  | buses |  | buses |  | Icc,0 (kA) |  | Icc,1 (kA) |  | b_0 |  | b_1 |  | q_cc,0 (deg) |  | q_cc,1 (deg) |  |  | relay
location | back | line | main | line | from | to | from | to | main | back | main | back | main | back | main | back | main | back | main | back | g_type_2 | q | line | g_type_3 |  |  | Pick-up settings
Near-end | 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 4.9937 | 0.81942 | 5.2131 | 1.047 | 2.4199 | 2.9393 | 2.3824 | 2.6526 | 271.5351 | 279.3957 | 272.3313 | 281.6854 | -0.20175 | 2 | 1 | -2.4208 | 2.2191 | 1 | 0.3
Near-end | 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 2.7751 | 1.0377 | 3.0056 | 1.2749 | 2.5921 | 5.5708 | 2.5138 | 4.7684 | 272.8691 | 277.6921 | 274.465 | 280.5753 | -0.33016 | 4 | 2 | -2.8133 | 2.4831 | 2 | 0.06
Near-end | 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 4.568 | 2.2469 | 4.7674 | 2.4489 | 1.6616 | 2.8243 | 1.6435 | 2.7249 | 272.0593 | 274.1894 | 272.8827 | 275.6184 | -0.11392 | 6 | 3 | -4.6312 | 4.5173 | 3 | 0.2
Near-end | 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 0.95627 | 0.18352 | 1.2334 | 0.75459 | 2.4589 | -26.1567 | 2.2462 | 6.041 | 277.2775 | 274.3646 | 280.7625 | 282.9413 | -2.7694 | 1 | 1 | -2.2105 | -0.55887 | 4 | 0.24
Near-end | 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 2.5332 | 0.61921 | 2.7676 | 0.90164 | 2.9009 | 6.1243 | 2.7934 | 4.5787 | 274.2842 | 281.3422 | 275.9168 | 284.4006 | -0.55809 | 3 | 2 | -2.496 | 1.938 | 5 | 0.08
Near-end | 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 0.87257 | 0.77634 | 1.1273 | 0.24751 | 4.6821 | 2.6647 | 3.9783 | 4.8699 | 279.7631 | 458.8036 | 282.875 | 290.4125 | 1.6248 | 5 | 3 | -1.4118 | 3.0366 | 6 | 0.2
Far-end | 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 1.0377 | 0.6192 | 1.2837 | 0.25781 | 5.5708 | 3.3511 | 4.7457 | 5.9122 | 277.6921 | 461.3423 | 280.7917 | 290.1458 | 1.4342 | 2 | 1 | -1.3391 | 2.7733
Far-end | 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 2.2469 | 0.77635 | 2.4892 | 1.0559 | 2.8243 | 7.2923 | 2.7068 | 5.4931 | 274.1893 | 278.8035 | 276.0684 | 282.1787 | -0.54091 | 4 | 2 | -2.5274 | 1.9864
Far-end | 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 0.81943 | 0.18351 | 1.0991 | 0.5646 | 2.9393 | -81.4237 | 2.6021 | 6.6752 | 279.3956 | 454.3647 | 282.7844 | 285.5202 | -2.0195 | 6 | 3 | -1.8483 | -0.17116
Far-end | 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 4.2735 | 2.5332 | 4.4774 | 2.7393 | 1.5719 | 2.9009 | 1.5542 | 2.8055 | 272.5381 | 274.2842 | 273.4252 | 275.604 | -0.12043 | 1 | 1 | -5.508 | 5.3875
Far-end | 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 3.1876 | 0.87257 | 3.4205 | 1.1143 | 2.6371 | 4.6821 | 2.5653 | 4.0056 | 272.6606 | 279.7631 | 274.0561 | 282.5399 | -0.33116 | 3 | 2 | -2.7474 | 2.4162
Far-end | 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 5.1335 | 0.95627 | 5.3438 | 1.1733 | 2.0878 | 2.4589 | 2.0614 | 2.285 | 271.3522 | 277.2775 | 272.1084 | 279.6458 | -0.17074 | 5 | 3 | -2.9022 | 2.7314
Objective function
[7 empty] | Type | Case | B | [5 empty] | D |  | S
|  |  |  | Rf=0 |  | 1 | 1 | 1 | -2.4199 | 0 | 0 | 0 | 2.9393 | 0 | 0.11293 |  | 0.2 | T212_0= | 0.33339
[6 empty] | 2 | 1 | 1 | 5.5708 | 0 | -2.5921 | 0 | 0 | 0 | 0.21209 |  | 0.2 | T111_0= | 0.27326
[6 empty] | 3 | 1 | 1 | 0 | 0 | 2.8243 | 0 | -1.6616 | 0 | 0.16554 | = | 0.2 | T422_0= | 0.48488
[6 empty] | 4 | 2 | 2 | 0 | 0 | 0.55809 | -2.7934 | 0 | 4.5787 | 0.18387 |  | 0.28387 | T321_0= | 0.42909
[6 empty] | 5 | 3 | 3 | 2.7694 | -2.2462 | 0 | 6.041 | 0 | 0 | 0.16101 |  | 0.94709 | T632_0= | 0.32151
[6 empty] | 6 | 3 | 4 | 0 | 4.8699 | 0 | 0 | 1.4118 | -3.9783 | 0.154 |  | 0.64753 | T531_0= | 0.26754
[6 empty] | 7 | 1 | 1 | 0 | -1.5719 | 0 | 2.9009 | 0 | 0 |  |  | 0.2 | Td= | 2.1097
[6 empty] | 8 | 1 | 1 | 7.2923 | 0 | -2.8243 | 0 | 0 | 0 |  |  | 0.35596
[6 empty] | 9 | 1 | 1 | 0 | 2.4589 | 0 | 0 | 0 | -2.0878 |  |  | 0.2
[6 empty] | 10 | 2 | 2 | 0 | 0 | 0.33116 | -2.5653 | 0 | 4.0056 |  |  | 0.2
[6 empty] | 11 | 3 | 4 | -4.7457 | 1.3391 | 0 | 0 | 5.9122 | 0 |  |  | 0.70006
[6 empty] | 12 | 3 | 5 | 0 | 0 | 6.6752 | 0 | -2.6021 | 1.8483 |  |  | 0.97065
|  |  |  | Rf=10 |  | 1 | 1 | 1 | -3.1025 | 0 | 0 | 0 | 3.9972 | 0 |  |  | 0.29326
[6 empty] | 2 | 1 | 1 | 9.9043 | 0 | -3.2783 | 0 | 0 | 0 |  |  | 0.57577
[6 empty] | 3 | 1 | 1 | 0 | 0 | 3.6802 | 0 | -1.935 | 0 |  |  | 0.29764
[6 empty] | 4 | 2 | 2 | 0 | 0 | 1.1715 | -3.1093 | 0 | 5.4732 |  |  | 0.46508
[6 empty] | 5 | 3 | 3 | 4.8085 | -2.322 | 0 | 6.5994 | 0 | 0 |  |  | 1.264
[6 empty] | 6 | 3 | 4 | 0 | 5.2197 | 0 | 0 | 1.0818 | -4.2103 |  |  | 0.63286
[6 empty] | 7 | 1 | 1 | 0 | -1.8092 | 0 | 3.7821 | 0 | 0 |  |  | 0.31169
[6 empty] | 8 | 1 | 1 | 17.4901 | 0 | -3.6802 | 0 | 0 | 0 |  |  | 1.3659
[6 empty] | 9 | 1 | 1 | 0 | 3.1662 | 0 | 0 | 0 | -2.5822 |  |  | 0.27386
[6 empty] | 10 | 2 | 2 | 0 | 0 | 0.78389 | -2.9131 | 0 | 4.9028 |  |  | 0.34914
[6 empty] | 11 | 3 | 4 | -5.1062 | 0.93277 | 0 | 0 | 6.4789 | 0 |  |  | 0.6644
[6 empty] | 12 | 3 | 5 | 0 | 0 | 7.319 | 0 | -2.6976 | 1.7427 |  |  | 1.0456

## RF=0
IEC 60255 SI Curve
[26 empty] | a1= | 0.14
[17 empty] | First Period |  | Second Period | [6 empty] | a2= | 0.02
Fault | relay |  | relay |  | buses |  | buses |  | Icc,0 (kA) |  | Icc,1 (kA) |  | b_0 |  | b_1 |  | q_cc,0 (deg) |  | q_cc,1 (deg) |  |  | relay
location | back | line | main | line | from | to | from | to | main | back | main | back | main | back | main | back | main | back | main | back | g_type_2 | q | line | g_type_3 |  |  | Pick-up settings
Near-end | 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 4.9937 | 0.81942 | 5.2131 | 1.047 | 2.4199 | 2.9393 | 2.3824 | 2.6526 | 271.5351 | 279.3957 | 272.3313 | 281.6854 | -0.20175 | 2 | 1 | -2.4208 | 2.2191 | 1 | 0.3
Near-end | 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 2.7751 | 1.0377 | 3.0056 | 1.2749 | 2.5921 | 5.5708 | 2.5138 | 4.7684 | 272.8691 | 277.6921 | 274.465 | 280.5753 | -0.33016 | 4 | 2 | -2.8133 | 2.4831 | 2 | 0.06
Near-end | 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 4.568 | 2.2469 | 4.7674 | 2.4489 | 1.6616 | 2.8243 | 1.6435 | 2.7249 | 272.0593 | 274.1894 | 272.8827 | 275.6184 | -0.11392 | 6 | 3 | -4.6312 | 4.5173 | 3 | 0.2
Near-end | 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 0.95627 | 0.18352 | 1.2334 | 0.75459 | 2.4589 | -26.1567 | 2.2462 | 6.041 | 277.2775 | 274.3646 | 280.7625 | 282.9413 | -2.7694 | 1 | 1 | -2.2105 | -0.55887 | 4 | 0.24
Near-end | 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 2.5332 | 0.61921 | 2.7676 | 0.90164 | 2.9009 | 6.1243 | 2.7934 | 4.5787 | 274.2842 | 281.3422 | 275.9168 | 284.4006 | -0.55809 | 3 | 2 | -2.496 | 1.938 | 5 | 0.08
Near-end | 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 0.87257 | 0.77634 | 1.1273 | 0.24751 | 4.6821 | 2.6647 | 3.9783 | 4.8699 | 279.7631 | 458.8036 | 282.875 | 290.4125 | 1.6248 | 5 | 3 | -1.4118 | 3.0366 | 6 | 0.2
Far-end | 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 1.0377 | 0.6192 | 1.2837 | 0.25781 | 5.5708 | 3.3511 | 4.7457 | 5.9122 | 277.6921 | 461.3423 | 280.7917 | 290.1458 | 1.4342 | 2 | 1 | -1.3391 | 2.7733
Far-end | 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 2.2469 | 0.77635 | 2.4892 | 1.0559 | 2.8243 | 7.2923 | 2.7068 | 5.4931 | 274.1893 | 278.8035 | 276.0684 | 282.1787 | -0.54091 | 4 | 2 | -2.5274 | 1.9864
Far-end | 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 0.81943 | 0.18351 | 1.0991 | 0.5646 | 2.9393 | -81.4237 | 2.6021 | 6.6752 | 279.3956 | 454.3647 | 282.7844 | 285.5202 | -2.0195 | 6 | 3 | -1.8483 | -0.17116
Far-end | 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 4.2735 | 2.5332 | 4.4774 | 2.7393 | 1.5719 | 2.9009 | 1.5542 | 2.8055 | 272.5381 | 274.2842 | 273.4252 | 275.604 | -0.12043 | 1 | 1 | -5.508 | 5.3875
Far-end | 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 3.1876 | 0.87257 | 3.4205 | 1.1143 | 2.6371 | 4.6821 | 2.5653 | 4.0056 | 272.6606 | 279.7631 | 274.0561 | 282.5399 | -0.33116 | 3 | 2 | -2.7474 | 2.4162
Far-end | 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 5.1335 | 0.95627 | 5.3438 | 1.1733 | 2.0878 | 2.4589 | 2.0614 | 2.285 | 271.3522 | 277.2775 | 272.1084 | 279.6458 | -0.17074 | 5 | 3 | -2.9022 | 2.7314
Objective function
Case | Constraint type: | [7 empty] | B | [5 empty] | D |  | S
3 | Type 3 j-i pair |  |  | relay q stuck in p1 (loss of sensitivity) |  |  |  | 1 | 2.7694 | -2.2462 | 0 | 6.041 | 0 | 0 | 0.11292 |  | 0.94707 | T212_0= | 0.33339
1 | Type 1 p-q pair | [6 empty] | 2 | -2.4199 | 0 | 0 | 0 | 2.9393 | 0 | 0.21209 |  | 0.19999 | T111_0= | 0.27326
2 | Type 2 j-i pair | [6 empty] | 3 | 0 | 0 | 0.55809 | -2.7934 | 0 | 4.5787 | 0.16553 | = | 0.28387 | T422_0= | 0.48487
1 | Type 1 p-q pair | [6 empty] | 4 | 5.5708 | 0 | -2.5921 | 0 | 0 | 0 | 0.18387 |  | 0.2 | T321_0= | 0.42908
4 | Type 3 j-i pair |  |  | relay q stuck in period 1 (out DZ) |  |  |  | 5 | 0 | 4.8699 | 0 | 0 | 1.4118 | -3.9783 | 0.16101 |  | 0.64751 | T632_0= | 0.32151
1 | Type 1 p-q pair | [6 empty] | 6 | 0 | 0 | 2.8243 | 0 | -1.6616 | 0 | 0.15399 |  | 0.2 | T531_0= | 0.26753
4 | Type 3 j-i pair |  |  | relay q stuck in period 1 (out DZ) |  |  |  | 7 | -4.7457 | 1.3391 | 0 | 0 | 5.9122 | 0 |  |  | 0.70004 | Td= | 2.1096
1 | Type 1 p-q pair | [6 empty] | 8 | 0 | -1.5719 | 0 | 2.9009 | 0 | 0 |  |  | 0.2
2 | Type 2 j-i pair | [6 empty] | 9 | 0 | 0 | 0.33116 | -2.5653 | 0 | 4.0056 |  |  | 0.2
1 | Type 1 p-q pair | [6 empty] | 10 | 7.2923 | 0 | -2.8243 | 0 | 0 | 0 |  |  | 0.35595
5 | Type 3 j-i pair |  |  | relay q stuck in period 1 (sesns a and out DZ) |  |  |  | 11 | 0 | 0 | 6.6752 | 0 | -2.6021 | 1.8483 |  |  | 0.97064
1 | Type 1 p-q pair | [6 empty] | 12 | 0 | 2.4589 | 0 | 0 | 0 | -2.0878 |  |  | 0.2
| 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 4.9937 | 0.81942 | 5.2131 | 1.047 | 2.4199 | 2.9393 | 2.3824 | 2.6526 | 271.5351 | 279.3957 | 272.3313 | 281.6854 | -0.20175 | 2 | 1 | -2.4208 | 2.2191
| 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 2.7751 | 1.0377 | 3.0056 | 1.2749 | 2.5921 | 5.5708 | 2.5138 | 4.7684 | 272.8691 | 277.6921 | 274.465 | 280.5753 | -0.33016 | 4 | 2 | -2.8133 | 2.4831
| 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 4.568 | 2.2469 | 4.7674 | 2.4489 | 1.6616 | 2.8243 | 1.6435 | 2.7249 | 272.0593 | 274.1894 | 272.8827 | 275.6184 | -0.11392 | 6 | 3 | -4.6312 | 4.5173
| 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 0.95627 | 0.18352 | 1.2334 | 0.75459 | 2.4589 | -26.1567 | 2.2462 | 6.041 | 277.2775 | 274.3646 | 280.7625 | 282.9413 | -2.7694 | 1 | 1 | -2.2105 | -0.55887
| 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 2.5332 | 0.61921 | 2.7676 | 0.90164 | 2.9009 | 6.1243 | 2.7934 | 4.5787 | 274.2842 | 281.3422 | 275.9168 | 284.4006 | -0.55809 | 3 | 2 | -2.496 | 1.938
| 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 0.87257 | 0.77634 | 1.1273 | 0.24751 | 4.6821 | 2.6647 | 3.9783 | 4.8699 | 279.7631 | 458.8036 | 282.875 | 290.4125 | 1.6248 | 5 | 3 | -1.4118 | 3.0366
| 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 1.0377 | 0.6192 | 1.2837 | 0.25781 | 5.5708 | 3.3511 | 4.7457 | 5.9122 | 277.6921 | 461.3423 | 280.7917 | 290.1458 | 1.4342 | 2 | 1 | -1.3391 | 2.7733
| 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 2.2469 | 0.77635 | 2.4892 | 1.0559 | 2.8243 | 7.2923 | 2.7068 | 5.4931 | 274.1893 | 278.8035 | 276.0684 | 282.1787 | -0.54091 | 4 | 2 | -2.5274 | 1.9864
| 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 0.81943 | 0.18351 | 1.0991 | 0.5646 | 2.9393 | -81.4237 | 2.6021 | 6.6752 | 279.3956 | 454.3647 | 282.7844 | 285.5202 | -2.0195 | 6 | 3 | -1.8483 | -0.17116
| 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 4.2735 | 2.5332 | 4.4774 | 2.7393 | 1.5719 | 2.9009 | 1.5542 | 2.8055 | 272.5381 | 274.2842 | 273.4252 | 275.604 | -0.12043 | 1 | 1 | -5.508 | 5.3875
| 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 3.1876 | 0.87257 | 3.4205 | 1.1143 | 2.6371 | 4.6821 | 2.5653 | 4.0056 | 272.6606 | 279.7631 | 274.0561 | 282.5399 | -0.33116 | 3 | 2 | -2.7474 | 2.4162
| 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 5.1335 | 0.95627 | 5.3438 | 1.1733 | 2.0878 | 2.4589 | 2.0614 | 2.285 | 271.3522 | 277.2775 | 272.1084 | 279.6458 | -0.17074 | 5 | 3 | -2.9022 | 2.7314
[9 empty] | 3.956 | 0.20022 | 3.9294 | 0.78918 | -3.1509 | -0.41184 | -2.3633 | -3.2596 | -6.1571 | -181.9466 | -8.4604 | -8.4604 | -1.6359 | 0 | 0 | -1.0817 | -0.55423
[9 empty] | 0.52817 | 0.26139 | 0.51635 | 0.21903 | -0.23224 | -1.7215 | -0.19307 | -0.72468 | -1.3203 | -1.1114 | -1.6034 | -1.6034 | 0.21075 | 0 | 0 | -0.28589 | 0.49664
[9 empty] | 3.7486 | 2.0634 | 3.6682 | 1.8843 | -1.2777 | 84.2481 | -0.95863 | -3.9503 | -7.3364 | -180.1753 | -9.9018 | -9.9018 | 1.9055 | 0 | 0 | -2.7829 | 4.6884
[9 empty] | -3.3172 | -2.3497 | -3.244 | -1.9847 | 0.88697 | -29.0577 | 0.69195 | 3.2354 | 4.7394 | 0.080374 | 7.3373 | 7.3373 | -2.6489 | 0 | 0 | 3.2975 | -5.9464
[9 empty] | -0.65439 | -0.25336 | -0.65291 | -0.2127 | 0.26385 | 1.4421 | 0.22818 | 0.57314 | 1.6236 | 1.5792 | 1.8607 | 1.8607 | -0.22693 | 0 | 0 | 0.25136 | -0.4783
[9 empty] | -4.2609 | -0.17992 | -4.2165 | -0.92578 | 2.5944 | 0.20579 | 1.9169 | 2.5849 | 8.4109 | 181.526 | 10.7667 | 10.7667 | 1.7955 | 0 | 0 | 1.4903 | 0.30518
Bus 4
G1
Line 1
G2
G3
Line 2
Line 3
Bus 1
Bus 2
Bus 3
Bus 5
Bus 6

## RF=10
IEC 60255 SI Curve
[26 empty] | a1= | 0.14
[17 empty] | First Period |  | Second Period | [6 empty] | a2= | 0.02
Fault | relay |  | relay |  | buses |  | buses |  | Icc,0 (kA) |  | Icc,1 (kA) |  | b_0 |  | b_1 |  | q_cc,0 (deg) |  | q_cc,1 (deg) |  |  | relay
location | back | line | main | line | from | to | from | to | main | back | main | back | main | back | main | back | main | back | main | back | g_type_2 | q | line | g_type_3 |  |  | Pick-up settings
Near-end | 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 2.726 | 0.44732 | 3.105 | 0.6236 | 3.1025 | 3.9972 | 2.9259 | 3.3393 | 326.0266 | 333.8872 | 323.4791 | 332.8332 | -0.34087 | 2 | 1 | -2.9859 | 2.6451 | 1 | 0.3
Near-end | 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 1.6184 | 0.60522 | 2.3142 | 0.98168 | 3.2783 | 9.9043 | 2.7894 | 5.8351 | 323.7265 | 328.5495 | 309.8567 | 315.9669 | -0.98988 | 4 | 2 | -3.2181 | 2.2282 | 2 | 0.06
Near-end | 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 2.6298 | 1.2935 | 2.984 | 1.5328 | 1.935 | 3.6802 | 1.8651 | 3.3677 | 323.6851 | 325.8153 | 321.3086 | 324.0443 | -0.36726 | 6 | 3 | -7.2589 | 6.8916 | 3 | 0.2
Near-end | 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 0.52202 | 0.10018 | 1.1206 | 0.68557 | 3.1662 | -8.0824 | 2.322 | 6.5994 | 331.769 | 328.8561 | 296.8041 | 298.9829 | -4.8085 | 1 | 1 | -2.2753 | -2.5332 | 4 | 0.24
Near-end | 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 1.4774 | 0.36113 | 2.1705 | 0.70711 | 3.7821 | 11.7761 | 3.1093 | 5.4732 | 325.1416 | 332.1996 | 308.7329 | 317.2167 | -1.1715 | 3 | 2 | -2.6952 | 1.5237 | 5 | 0.08
Near-end | 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 0.50233 | 0.44693 | 1.0264 | 0.22537 | 7.5311 | 3.4164 | 4.2103 | 5.2197 | 331.3889 | 510.4294 | 297.4225 | 304.96 | 1.8746 | 5 | 3 | -1.0818 | 2.9564 | 6 | 0.2
Far-end | 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 0.60523 | 0.36113 | 1.16 | 0.23298 | 9.9042 | 4.5747 | 5.1062 | 6.4789 | 328.5494 | 512.1996 | 297.4129 | 306.767 | 1.6296 | 2 | 1 | -0.93277 | 2.5623
Far-end | 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 1.2935 | 0.44694 | 2.0173 | 0.85573 | 3.6802 | 17.4901 | 2.9593 | 6.6085 | 325.8153 | 330.4295 | 306.3039 | 312.4142 | -1.4372 | 4 | 2 | -2.7112 | 1.274
Far-end | 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 0.44732 | 0.10018 | 1.0041 | 0.51579 | 3.9972 | -10.1949 | 2.6976 | 7.319 | 333.8871 | 508.8561 | 297.0138 | 299.7496 | -3.5965 | 6 | 3 | -1.7427 | -1.8538
Far-end | 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 2.4923 | 1.4774 | 2.8917 | 1.7692 | 1.8092 | 3.7821 | 1.7372 | 3.4346 | 323.3954 | 325.1416 | 319.8584 | 322.0372 | -0.51576 | 1 | 1 | -9.5101 | 8.9943
Far-end | 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 1.8351 | 0.50233 | 2.5089 | 0.81736 | 3.3716 | 7.5311 | 2.9131 | 4.9028 | 324.2866 | 331.389 | 312.9749 | 321.4587 | -0.78389 | 3 | 2 | -3.1797 | 2.3958
Far-end | 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 2.8023 | 0.52202 | 3.139 | 0.68921 | 2.5822 | 3.1662 | 2.473 | 2.798 | 325.8437 | 331.769 | 324.0544 | 331.5919 | -0.29574 | 5 | 3 | -3.8281 | 3.5324
Objective function
[5 empty] | Case | Constraint type: |  |  | B | [5 empty] | D |  | S
[5 empty] | 1 | 1 |  | 1 | -3.1025 | 0 | 0 | 0 | 3.9972 | 0 | 0.1 |  | 0.2 | T212_0= | 0.26184
[5 empty] | 1 | 1 |  | 2 | 9.9043 | 0 | -3.2783 | 0 | 0 | 0 | 0.14472 |  | 0.59223 | T111_0= | 0.31025
[5 empty] | 1 | 1 |  | 3 | 0 | 0 | 3.6802 | 0 | -1.935 | 0 | 0.12146 | = | 0.2 | T422_0= | 0.41172
[5 empty] | 2 | 2 |  | 4 | 0 | 0 | 1.1715 | -3.1093 | 0 | 5.4732 | 0.12211 |  | 0.30993 | T321_0= | 0.3982
[5 empty] | 3 | 3 |  | 5 | 4.8085 | -2.322 | 0 | 6.5994 | 0 | 0 | 0.12765 |  | 0.95067 | T632_0= | 0.25822
[5 empty] | 4 | 3 |  | 6 | 0 | 5.2197 | 0 | 0 | 1.0818 | -4.2103 | 0.1 |  | 0.47248 | T531_0= | 0.24701
[5 empty] | 1 | 1 |  | 7 | 0 | -1.8092 | 0 | 3.7821 | 0 | 0 |  |  | 0.2 | Td= | 1.8872
[5 empty] | 1 | 1 |  | 8 | 0 | 0 | 0 | -3.3716 | 0 | 7.5311 |  |  | 0.3414
[5 empty] | 1 | 1 |  | 9 | 0 | 3.1662 | 0 | 0 | 0 | -2.5822 |  |  | 0.2
[5 empty] | 2 | 3 |  | 10 | 6.6085 | 0 | -2.9593 | 1.4372 | 0 | 0 |  |  | 0.47691
[5 empty] | 4 | 3 |  | 11 | -5.1062 | 0.93277 | 0 | 0 | 6.4789 | 0 |  |  | 0.45141
[5 empty] | 5 | 3 |  | 12 | 0 | 0 | 7.319 | 0 | -2.6976 | 1.7427 |  |  | 0.71891
| 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 4.9937 | 0.81942 | 5.2131 | 1.047 | 2.4199 | 2.9393 | 2.3824 | 2.6526 | 271.5351 | 279.3957 | 272.3313 | 281.6854 | -0.20175 | 2 | 1 | -2.4208 | 2.2191
| 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 2.7751 | 1.0377 | 3.0056 | 1.2749 | 2.5921 | 5.5708 | 2.5138 | 4.7684 | 272.8691 | 277.6921 | 274.465 | 280.5753 | -0.33016 | 4 | 2 | -2.8133 | 2.4831
| 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 4.568 | 2.2469 | 4.7674 | 2.4489 | 1.6616 | 2.8243 | 1.6435 | 2.7249 | 272.0593 | 274.1894 | 272.8827 | 275.6184 | -0.11392 | 6 | 3 | -4.6312 | 4.5173
| 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 0.95627 | 0.18352 | 1.2334 | 0.75459 | 2.4589 | -26.1567 | 2.2462 | 6.041 | 277.2775 | 274.3646 | 280.7625 | 282.9413 | -2.7694 | 1 | 1 | -2.2105 | -0.55887
| 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 2.5332 | 0.61921 | 2.7676 | 0.90164 | 2.9009 | 6.1243 | 2.7934 | 4.5787 | 274.2842 | 281.3422 | 275.9168 | 284.4006 | -0.55809 | 3 | 2 | -2.496 | 1.938
| 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 0.87257 | 0.77634 | 1.1273 | 0.24751 | 4.6821 | 2.6647 | 3.9783 | 4.8699 | 279.7631 | 458.8036 | 282.875 | 290.4125 | 1.6248 | 5 | 3 | -1.4118 | 3.0366
| 5 | 1 | 1 | 1 | 3 | 6 | 1 | 4 | 0.60523 | 0.36113 | 1.16 | 0.23298 | 9.9042 | 4.5747 | 5.1062 | 6.4789 | 328.5494 | 512.1996 | 297.4129 | 306.767 | 1.6296 | 2 | 1 | -0.93277 | 2.5623
| 1 | 2 | 3 | 2 | 1 | 4 | 2 | 5 | 1.2935 | 0.44694 | 2.0173 | 0.85573 | 3.6802 | 17.4901 | 2.9593 | 6.6085 | 325.8153 | 330.4295 | 306.3039 | 312.4142 | -1.4372 | 4 | 2 | -2.7112 | 1.274
| 3 | 3 | 5 | 3 | 2 | 5 | 3 | 6 | 0.44732 | 0.10018 | 1.0041 | 0.51579 | 3.9972 | -10.1949 | 2.6976 | 7.319 | 333.8871 | 508.8561 | 297.0138 | 299.7496 | -3.5965 | 6 | 3 | -1.7427 | -1.8538
| 4 | 1 | 2 | 1 | 3 | 5 | 2 | 4 | 2.4923 | 1.4774 | 2.8917 | 1.7692 | 1.8092 | 3.7821 | 1.7372 | 3.4346 | 323.3954 | 325.1416 | 319.8584 | 322.0372 | -0.51576 | 1 | 1 | -9.5101 | 8.9943
| 6 | 2 | 4 | 2 | 1 | 6 | 3 | 5 | 1.8351 | 0.50233 | 2.5089 | 0.81736 | 3.3716 | 7.5311 | 2.9131 | 4.9028 | 324.2866 | 331.389 | 312.9749 | 321.4587 | -0.78389 | 3 | 2 | -3.1797 | 2.3958
| 2 | 3 | 6 | 3 | 2 | 4 | 1 | 6 | 2.8023 | 0.52202 | 3.139 | 0.68921 | 2.5822 | 3.1662 | 2.473 | 2.798 | 325.8437 | 331.769 | 324.0544 | 331.5919 | -0.29574 | 5 | 3 | -3.8281 | 3.5324
[9 empty] | 4.3885 | 0.45829 | 4.0531 | 0.81401 | -7.4844 | -1.6354 | -2.7239 | -3.8263 | -57.0144 | -232.8039 | -25.0816 | -25.0816 | -1.8313 | 0 | 0 | -1.4881 | -0.34324
[9 empty] | 1.4815 | 0.59081 | 0.98823 | 0.4192 | -1.0881 | -11.9193 | -0.4455 | -1.8402 | -52.9463 | -52.7374 | -31.8389 | -31.8389 | 1.107 | 0 | 0 | -0.10209 | 1.2091
[9 empty] | 4.1207 | 2.1467 | 3.7633 | 1.9331 | -2.3357 | 13.0192 | -1.0541 | -4.5941 | -61.8279 | -234.6668 | -24.1312 | -24.1312 | 3.4826 | 0 | 0 | -2.8885 | 6.3711
[9 empty] | -1.5361 | -1.2939 | -1.6583 | -1.0146 | 0.64967 | -29.9388 | 0.50892 | 2.6063 | -46.1179 | -50.777 | -39.0959 | -39.0959 | -2.2536 | 0 | 0 | 7.2996 | -9.5532
[9 empty] | 0.69813 | 0.11688 | 0.2587 | 0.08428 | -0.47071 | -1.4069 | -0.11968 | -0.32402 | -50.0023 | -50.0468 | -37.0581 | -37.0581 | 0.22581 | 0 | 0 | 0.68364 | -0.45784
[9 empty] | -1.9298 | 0.25433 | -2.0117 | -0.4417 | 2.0999 | -0.50151 | 1.5053 | 2.0719 | -46.0806 | 127.0345 | -41.1794 | -41.1794 | 1.9205 | 0 | 0 | 2.4163 | -0.49579
Bus 4
G1
Line 1
G2
G3
Line 2
Line 3
Bus 1
Bus 2
Bus 3
Bus 5
Bus 6